{"text_format":"1","workbook":"xlsx","n_sheets":38,"sheets":["ネットワーク図","Sheet1","Sheet2","Sheet3","Sheet4","Sheet5","Sheet6","Sheet7","Sheet8","Sheet9","Sheet10","Sheet11","Sheet12","Sheet13","Sheet14","Sheet15","Sheet16","Sheet17","Sheet18","Sheet19","Sheet20","全G稼働解析結果","パイプデータ","需要量","条件","導管","INPUTDATA","絵 (3)","絵 (2)","絵","製造曲線","大口需要曲線","一般需要曲線","非定常解析結果","No.2G停止解析結果","Sheet23","Sheet22","Sheet21"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":2,"comments":2,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"ネットワーク図","index":0,"n_rows":58,"n_cols":14761,"rows_kept":58,"cut":false,"hidden":false,"merged":[[0,22,0,36],[0,39,0,40],[9,33,9,34],[9,35,9,36],[10,33,10,34],[10,35,10,36],[7,28,7,29],[7,30,7,31],[7,33,7,34],[7,35,7,36],[8,33,8,34],[8,35,8,36],[5,28,5,29],[5,30,5,31],[5,33,5,34],[5,35,5,36],[6,28,6,29],[6,30,6,31],[6,33,6,34],[6,35,6,36],[4,35,4,36],[4,28,4,29],[4,30,4,31],[4,33,4,34],[3,23,3,24],[3,25,3,26],[3,28,3,29],[3,30,3,31],[3,33,3,34],[12,22,13,40],[1,22,1,24],[2,23,2,24],[2,25,2,26],[2,28,2,29],[2,30,2,31],[2,33,2,34],[2,35,2,36],[1,25,1,26],[1,28,1,29],[1,30,1,31],[1,33,1,34],[1,35,1,36],[3,35,3,36],[4,23,4,24],[4,25,4,26]]}
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"解析条件",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"解析結果"]
["","","","","","","","","","","","","","","","","","","","","","","①ガス比重",null,null,0.64,null,"ノード番号","④負荷量(㎥/h)",null,"⑤標高（ｍ）",null,"パイプ番号","⑥内径（ｃｍ）",null,"⑦延長（ｍ）",null,null,"","ノード番号/ガバナ名","⑧圧力（kPa)","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","","",""]
[null,null,null,null,null,"","","","","","","",null,null,null,null,null,null,null,null,null,null,"ガバナ名","②ガバナ設定圧力（kPa)",null,"③標高（ｍ）",null,"N001",30,null,30,null,"P001",5,null,50,null,null,null,"N001",2.2759999999999998]
[null,null,null,null,null,"","","","","","","",null,null,null,null,null,null,null,null,null,null,"エナジー",2.2999999999999998,null,30,null,"N002",60,null,30,null,"P002",5,null,50,null,null,null,"N002",1.496]
[null,null,null,null,null,"","","","","","","",null,null,null,null,null,null,null,null,null,null,"ソリューション",2.2999999999999998,null,30,null,"N003",210,null,20,null,"P003",5,null,30,null,null,null,"N003",1.4490000000000001]
[null,null,null,null,null,"","","","","","","",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"N004",150,null,10,null,"P004",10,null,30,null,null,null,"N004",1.9419999999999999]
[null,null,null,null,null,"","","","","","","",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"N005",80,null,30,null,"P005",5,null,20,null,null,null,"N005",1.9219999999999999]
[null,null,null,null,null,"","","","","","","",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"N006",30,null,20,null,"P006",5,null,50,null,null,null,"N006",2.2450000000000001]
[null,null,null,null,null,"","","","","","","",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P007",5,null,10,null,null,null,"エナジー",2.2999999999999998]
[null,null,null,null,null,"","","","","","","",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P101",20,null,50,null,null,null,"ソリューション",2.2999999999999998]
[null,null,null,null,null,"","","","","","","",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P102",20,null,50]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","","",null,null,null,null,null,null,null,null,null,null,"ネットワーク図"]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","","",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"H51","v":"色"},{"$f":"I51","v":"下限圧力"},"上限圧力"]
[null,null,null,null,null,"","","","","","","",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"H52","v":"BRUE"},"2.00kPa","10.00kPa"]
[null,null,null,null,null,"","","","","","","",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GREEN","1.80kPa","1.99kPa"]
[null,null,null,null,null,"","","","","","","",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"PINK","1.50kPa","1.79kPa"]
[null,null,null,null,null,"","","","","","","",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"RED","-10kPa","1.49kPa"]
[null,null,null,null,null,"","","","","","","",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","","",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"H56","v":""},{"$f":"I56","v":""}]
[null,null,null,null,null,"","","","","","","",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","色","下限圧力","上限圧力","",""]
[null,null,null,null,null,"","","BRUE","2.00kPa","10.00kPa","",""]
[null,null,null,null,null,"","","GREEN","1.80kPa","1.99kPa","",""]
[null,null,null,null,null,"","","PINK","1.50kPa","1.79kPa","",""]
[null,null,null,null,null,"","","RED","-10kPa","1.49kPa","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]
[null,null,null,null,null,"","","","","","",""]

{"sheet":"Sheet1","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet2","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet3","index":3,"n_rows":11,"n_cols":4,"rows_kept":11,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,"繰返計算回数=",22]
[null,null,4.4408920985006262E-16]
[null,null,6.7164283024112592E-9]

{"sheet":"Sheet4","index":4,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet5","index":5,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet6","index":6,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet7","index":7,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet8","index":8,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet9","index":9,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet10","index":10,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet11","index":11,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet12","index":12,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet13","index":13,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet14","index":14,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet15","index":15,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet16","index":16,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet17","index":17,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet18","index":18,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet19","index":19,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet20","index":20,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"全G稼働解析結果","index":21,"n_rows":34,"n_cols":40,"rows_kept":34,"cut":false,"hidden":false,"merged":[]}
["＊＊＊　全G稼働解析結果　＊＊＊",null,null,null,null,null,null,null,"＊＊　全ノードデータ　　＊＊",null,null,null,null,null,null,null,null,"＊＊　大口ノードデータ　　＊＊",null,null,null,null,null,null,null,null,"＊＊　パイプデータ　　＊＊",null,null,null,null,null,null,null,null,"＊＊　口径別延長集計　　＊＊"]
["FILE NAME: "]
[" DATE: ","R4/12/12",null,null,null,null,null,null,"ノードID","標高(m)","需要量(m3/h)",null,"圧力(ｋPa)","標高補正圧力(ｋPa)","標高補正後圧力(ｋPa)",null,null,"ノードID",null,"需要量(m3/h)",null,"圧力(ｋPa)",null,null,null,null,"ﾊﾟｲﾌﾟ","上流","下流","内径","延長","流量","ﾊﾟｲﾌﾟ幾何容積",null,null,"口径（A)",null,"本数",null,"合計延長(m)"]
[" TIME: ","16:35:34","->","16:35:34",null,null,null,null,"N001",30,30,null,2.1389999999999998,0.13694398105144501,2.2759999999999998,null,null,"合計",null,0,null,null,null,null,null,null,"ID","ﾉｰﾄﾞID","ﾉｰﾄﾞID","(mm)","(m)","(m3/h)","(m3)",null,null,"50未満",null,0,null,0]
[null,null,null,null,null,null,null,null,"N002",30,60,null,1.359,0.13694398105144501,1.496,null,null,null,null,null,null,null,null,null,null,null,"P001","N001","N002",5,50,62.3,9.8000000000000004E-2,null,null,50,null,6,null,210]
[null,null,null,null,null,null,null,null,"N003",20,210,null,1.3580000000000001,9.1295987367630005E-2,1.4490000000000001,null,null,null,null,null,null,null,null,null,null,null,"P002","N002","N003",5,50,2.2999999999999998,9.8000000000000004E-2,null,null,100,null,1,null,30]
[null,null,null,null,null,null,null,null,"N004",10,150,null,1.8959999999999999,4.5647993683815002E-2,1.9419999999999999,null,null,null,null,null,null,null,null,null,null,null,"P003","N004","N003",5,30,66.900000000000006,5.8999999999999997E-2,null,null,150,null,0,null,0]
[null,null,null,null,null,null,null,null,"N005",30,80,null,1.7849999999999999,0.13694398105144501,1.9219999999999999,null,null,null,null,null,null,null,null,null,null,null,"P004","N001","N004",10,30,254,0.23599999999999999,null,null,200,null,2,null,100]
[null,null,null,null,null,null,null,null,"N006",20,30,null,2.1539999999999999,9.1295987367630005E-2,2.2450000000000001,null,null,null,null,null,null,null,null,null,null,null,"P005","N004","N005",5,20,37.200000000000003,3.9E-2,null,null,250,null,0,null,0]
[null,null,null,null,null,null,null,null,"エナジー",30,0,null,2.1629999999999998,0.13694398105144501,2.2999999999999998,null,null,null,null,null,null,null,null,null,null,null,"P006","N006","N005",5,50,42.8,9.8000000000000004E-2,null,null,300,null,0,null,0]
[null,null,null,null,null,null,null,null,"ソリューション",30,0,null,2.1629999999999998,0.13694398105144501,2.2999999999999998,null,null,null,null,null,null,null,null,null,null,null,"P007","N006","N003",5,10,140.80000000000001,0.02,null,null,350,null,0,null,0]
[null,null,null,null,null,null,null,null,"需要量合計(m3/h)",null,560,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P101","エナジー","N001",20,50,346.4,1.571,null,null,400,null,0,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P102","ソリューション","N006",20,50,213.6,1.571,null,null,450,null,0,null,0]
["＊＊　流量係数　K=K(D)*a ＊＊",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,340,null,3.79,null,null,500,null,0,null,0]
["1 Pole        K(D) = KG-Pole",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,550,null,0,null,0]
["流量補正係数　a= ",null,1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,600,null,0,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,650,null,0,null,0]
["許容誤差",null,1E-8,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null," 700以上",null,0,null,0]
["設定最大繰り返し計算数",null,30000]
["繰り返し計算数",null,40]
[]
["比重",null,0.64]
["総ノード数",null,8]
["一般ノード数",null,8]
["大口ノード数",null,0]
["パイプ数",null,9]
["ガバナ数",null,2]
[]
[]
["＊＊　ガバナデータ　　＊＊"]
["ガバナID","ガバナ設定圧力（ｋPa）","ガバナ標高(m)","ガバナ標高補正圧力(kPa)","ガバナ標高補正後圧力(kPa)","ガバナ送出量(m3/h)"]
["エナジー",2.1629999999999998,30,0.13700000000000001,2.2999999999999998,346.4]
["ソリューション",2.1629999999999998,30,0.13700000000000001,2.2999999999999998,213.6]
["ガバナ送出量合計(m3/h)",null,null,null,null,560]

{"sheet":"パイプデータ","index":22,"n_rows":13,"n_cols":15,"rows_kept":13,"cut":false,"hidden":false,"merged":[[1,5,2,5],[1,6,2,6],[1,14,2,14]]}
["３．パイプデータ",null,null,null,null,null,null,null,"CELLS(3+i,9)","CELLS(3+i,10)","CELLS(3+i,11)","CELLS(3+i,12)","CELLS(3+i,13)","CELLS(3+i,14)","CELLS(3+i,15)"]
["ﾊﾟｲﾌﾟ","上流","下流","内径","延長","遮断","KG-Pole\n流量係数",null,"ﾊﾟｲﾌﾟ","上流","下流","内径","延長","遮断有無","KG-Pole流量係数"]
["パイプID","ﾉｰﾄﾞID","ﾉｰﾄﾞID","[cm]"," [ｍ]",null,null,null,"ﾊﾟｲﾌﾟID","ﾉｰﾄﾞID","ﾉｰﾄID","[cm]"," [ｍ]"]
["P001","N001","N002",{"$f":"ネットワーク図!AH3","v":5},{"$f":"ネットワーク図!AJ3","v":50},null,{"$f":"IF(D4>0,HLOOKUP(D4,INPUTDATA!$K$9:$O$11,3,TRUE),\"\")","v":0.70699999999999996},null,{"$f":"IF(A4=\"\",\"\",A4)","v":"P001"},{"$f":"IF(B4=\"\",\"\",B4)","v":"N001"},{"$f":"IF(C4=\"\",\"\",C4)","v":"N002"},{"$f":"IF(D4=\"\",\"\",IF(F4=\"遮断\",0.3,D4))","v":5},{"$f":"IF(E4=\"\",\"\",E4)","v":50},{"$f":"IF(F4=\"\",\"\",F4)","v":""},{"$f":"IF(G4=\"\",\"\",G4)","v":0.70699999999999996}]
["P002","N002","N003",{"$f":"ネットワーク図!AH4","v":5},{"$f":"ネットワーク図!AJ4","v":50},null,{"$f":"IF(D5>0,HLOOKUP(D5,INPUTDATA!$K$9:$O$11,3,TRUE),\"\")","v":0.70699999999999996},null,"P002","N002","N003",{"$f":"IF(D5=\"\",\"\",IF(F5=\"遮断\",0.3,D5))","v":5},{"$f":"IF(E5=\"\",\"\",E5)","v":50},{"$f":"IF(F5=\"\",\"\",F5)","v":""},{"$f":"IF(G5=\"\",\"\",G5)","v":0.70699999999999996}]
["P003","N003","N004",{"$f":"ネットワーク図!AH5","v":5},{"$f":"ネットワーク図!AJ5","v":30},null,{"$f":"IF(D6>0,HLOOKUP(D6,INPUTDATA!$K$9:$O$11,3,TRUE),\"\")","v":0.70699999999999996},null,"P003","N003","N004",{"$f":"IF(D6=\"\",\"\",IF(F6=\"遮断\",0.3,D6))","v":5},30,"",0.70699999999999996]
["P004","N001","N004",{"$f":"ネットワーク図!AH6","v":10},{"$f":"ネットワーク図!AJ6","v":30},null,{"$f":"IF(D7>0,HLOOKUP(D7,INPUTDATA!$K$9:$O$11,3,TRUE),\"\")","v":0.70699999999999996},null,"P004","N001","N004",{"$f":"IF(D7=\"\",\"\",IF(F7=\"遮断\",0.3,D7))","v":10},30,"",0.70699999999999996]
["P005","N004","N005",{"$f":"ネットワーク図!AH7","v":5},{"$f":"ネットワーク図!AJ7","v":20},null,{"$f":"IF(D8>0,HLOOKUP(D8,INPUTDATA!$K$9:$O$11,3,TRUE),\"\")","v":0.70699999999999996},null,"P005","N004","N005",5,20,"",0.70699999999999996]
["P006","N006","N005",{"$f":"ネットワーク図!AH8","v":5},{"$f":"ネットワーク図!AJ8","v":50},null,{"$f":"IF(D9>0,HLOOKUP(D9,INPUTDATA!$K$9:$O$11,3,TRUE),\"\")","v":0.70699999999999996},null,"P006","N006","N005",5,50,"",0.70699999999999996]
["P007","N006","N003",{"$f":"ネットワーク図!AH9","v":5},{"$f":"ネットワーク図!AJ9","v":10},null,{"$f":"IF(D10>0,HLOOKUP(D10,INPUTDATA!$K$9:$O$11,3,TRUE),\"\")","v":0.70699999999999996},null,"P007","N006","N003",5,{"$f":"IF(E10=\"\",\"\",E10)","v":10},"",{"$f":"IF(G10=\"\",\"\",G10)","v":0.70699999999999996}]
["P101","エナジー","N001",{"$f":"ネットワーク図!AH10","v":20},{"$f":"ネットワーク図!AJ10","v":50},null,{"$f":"IF(D11>0,HLOOKUP(D11,INPUTDATA!$K$9:$O$11,3,TRUE),\"\")","v":0.70699999999999996},null,"P101","エナジー","N001",20,50,"",0.70699999999999996]
["P102","ソリューション","N006",{"$f":"ネットワーク図!AH11","v":20},{"$f":"ネットワーク図!AJ11","v":50},null,{"$f":"IF(D12>0,HLOOKUP(D12,INPUTDATA!$K$9:$O$11,3,TRUE),\"\")","v":0.70699999999999996},null,"P102","ソリューション","N006",20,50,"",0.70699999999999996]
[null,null,null,null,null,null,{"$f":"IF(D13>0,HLOOKUP(D13,INPUTDATA!$K$9:$O$11,3,TRUE),\"\")","v":""},null,"","","","","","",""]

{"sheet":"需要量","index":23,"n_rows":242,"n_cols":12,"rows_kept":242,"cut":false,"hidden":false,"merged":[]}
["ノードID","標高（ｍ）","需要量（ｍ３/h)","基本需要量データ×需要倍率","基本需要量データ"]
["N001",{"$f":"ネットワーク図!AE3","v":30},{"$f":"E2","v":30},{"$f":"E2*$L$3","v":30},{"$f":"ネットワーク図!AC3","v":30},null,"需要量（補正前）","需要量（補正後）","補正係数","判定","ノード数","需要倍率"]
["N002",{"$f":"ネットワーク図!AE4","v":30},{"$f":"ネットワーク図!AC4","v":60},60,{"$f":"ネットワーク図!AC4","v":60},null,{"$f":"ROUND(SUM(C2:C164),4)","v":560},{"$f":"ROUND((INPUTDATA!B16)/24,4)*L3","v":560},{"$f":"ROUND(H3/G3,3)","v":1},{"$f":"IF(I3=1,\"ＯＫ\",\"ＮＧ\")","v":"ＯＫ"},{"$f":"COUNTIF(A:A,\"*\")+COUNTIF(A:A,\">=0\")","v":9},1]
["N003",{"$f":"ネットワーク図!AE5","v":20},{"$f":"ネットワーク図!AC5","v":210},210,{"$f":"ネットワーク図!AC5","v":210},null,{"$f":"SUM(E2:E164)*24","v":13440}]
["N004",{"$f":"ネットワーク図!AE6","v":10},{"$f":"ネットワーク図!AC6","v":150},150,{"$f":"ネットワーク図!AC6","v":150}]
["N005",{"$f":"ネットワーク図!AE7","v":30},{"$f":"ネットワーク図!AC7","v":80},80,{"$f":"ネットワーク図!AC7","v":80}]
["N006",{"$f":"ネットワーク図!AE8","v":20},{"$f":"ネットワーク図!AC8","v":30},30,{"$f":"ネットワーク図!AC8","v":30}]
["エナジー",{"$f":"ネットワーク図!Z4","v":30},{"$f":"E8","v":0},0,0]
["ソリューション",{"$f":"ネットワーク図!Z5","v":30},{"$f":"E9","v":0},0,0]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,{"$f":"E235*$L$3","v":0}]
[null,null,null,0]
[null,null,null,0]
[null,null,null,0]
[null,null,{"$f":"D239","v":0},0]
[null,null,0,0]
[null,null,0,0]
[null,null,0,0]

{"sheet":"条件","index":24,"n_rows":64,"n_cols":13,"rows_kept":64,"cut":false,"hidden":false,"merged":[]}
["２．データ"]
["（１）圧力(１：低圧、２：中圧）",null,null,1]
["（２）ノード・パイプデータ"]
[null,"①一般需要ノード数",null,{"$f":"COUNTA(需要量!A2:A242)","v":8}]
[null,"②大口需要ノード数",null,0]
[null,"③パイプ数",null,{"$f":"COUNTA(パイプデータ!A4:A814)-COUNTIF(パイプデータ!F4:F814,\"遮断\")","v":9}]
[null,"④ガバナ数",null,{"$f":"COUNTA(C15:C64)","v":2},null,null,null,null,"P　標高補正圧力（kPa）","h 標高（ｍ）","A 空気密度(kg/m3)","S ガス比重","g 重力加速度(m/s²)"]
[null,null,null,null,null,null,null,null,"P＝h×A×(1-S)×ｇ/1000","需要量シートに入力",1.2929999999999999,{"$f":"D9","v":0.64},9.8066499999999994]
["（３）比重データ",null,null,{"$f":"ネットワーク図!Z2","v":0.64}]
["（４）収束データ"]
[null,"①最大反復回数",null,30000]
[null,"②収束判定値",null,1E-8]
["（５）ガバナデータ",null,null,null,null,null,null,null,null,null,null,"計算上のｶﾞﾊﾞﾅ設定検討"]
[null,"No","ﾉｰﾄﾞID",{"$f":"IF(D2=1,\"圧力(kPa)\",IF(D2=2,\"圧力(MPa)\",\"\"))","v":"圧力(kPa)"},null,null,"ﾉｰﾄﾞ ID","①ガバナ設定圧力(kPa)","h 標高（ｍ）","④ガバナ最終設定圧力","②P 標高補正値(kPa)","①-②ガバナ標高補正圧力(kPa)","③ガバナ停止後着圧(kPa)"]
[null,1,{"$f":"ネットワーク図!W4","v":"エナジー"},{"$f":"ネットワーク図!X4","v":2.2999999999999998},null,null,{"$f":"IF(C15<>\"\",C15,\"\")","v":"エナジー"},{"$f":"IF(D15<>\"\",D15,\"\")","v":2.2999999999999998},{"$f":"IFERROR(VLOOKUP(G15,需要量!$A$2:$B$313,2,FALSE),\"\")","v":30},{"$f":"IFERROR(LARGE((L15,M15),1),\"\")","v":2.1630560167399997},{"$f":"IFERROR(I15*$K$8*(1-$L$8)*$M$8/1000,\"\")","v":0.13694398325999999},{"$f":"IFERROR(H15-K15,\"\")","v":2.1630560167399997},-4.0999999046325684]
[null,2,{"$f":"ネットワーク図!W5","v":"ソリューション"},{"$f":"ネットワーク図!X5","v":2.2999999999999998},null,null,{"$f":"IF(C16<>\"\",C16,\"\")","v":"ソリューション"},{"$f":"IF(D16<>\"\",D16,\"\")","v":2.2999999999999998},{"$f":"IFERROR(VLOOKUP(G16,需要量!$A$2:$B$313,2,FALSE),\"\")","v":30},{"$f":"IFERROR(LARGE((L16,M16),1),\"\")","v":2.1630560167399997},{"$f":"IFERROR(I16*$K$8*(1-$L$8)*$M$8/1000,\"\")","v":0.13694398325999999},{"$f":"IFERROR(H16-K16,\"\")","v":2.1630560167399997},-0.71899998188018799]
[null,3,null,{"$f":"IF(E17=\"\",\"\",E17*1.02064*100)","v":""},null,null,"",{"$f":"IF(D17<>\"\",D17,\"\")","v":""},{"$f":"IFERROR(VLOOKUP(G17,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L17,M17),1),\"\")","v":""},"",""]
[null,4,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G18,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L18,M18),1),\"\")","v":""},"",""]
[null,5,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G19,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L19,M19),1),\"\")","v":""},"",""]
[null,6,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G20,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L20,M20),1),\"\")","v":""},"",""]
[null,7,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G21,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L21,M21),1),\"\")","v":""},"",""]
[null,8,null,{"$f":"IF(E22=\"\",\"\",E22*1.02064*100)","v":""},null,null,"","",{"$f":"IFERROR(VLOOKUP(G22,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L22,M22),1),\"\")","v":""},"",""]
[null,9,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G23,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L23,M23),1),\"\")","v":""},"",""]
[null,10,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G24,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L24,M24),1),\"\")","v":""},"",""]
[null,11,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G25,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L25,M25),1),\"\")","v":""},"",""]
[null,12,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G26,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L26,M26),1),\"\")","v":""},"",""]
[null,13,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G27,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L27,M27),1),\"\")","v":""},"",""]
[null,14,null,{"$f":"IF(E28=\"\",\"\",E28*1.02064*100)","v":""},null,null,"","",{"$f":"IFERROR(VLOOKUP(G28,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L28,M28),1),\"\")","v":""},"",""]
[null,15,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G29,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L29,M29),1),\"\")","v":""},"",""]
[null,16,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G30,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L30,M30),1),\"\")","v":""},"",""]
[null,17,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G31,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L31,M31),1),\"\")","v":""},"",""]
[null,18,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G32,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L32,M32),1),\"\")","v":""},"",""]
[null,19,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G33,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L33,M33),1),\"\")","v":""},"",""]
[null,20,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G34,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L34,M34),1),\"\")","v":""},"",""]
[null,21,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G35,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L35,M35),1),\"\")","v":""},"",""]
[null,22,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G36,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L36,M36),1),\"\")","v":""},"",""]
[null,23,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G37,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L37,M37),1),\"\")","v":""},"",""]
[null,24,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G38,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L38,M38),1),\"\")","v":""},"",""]
[null,25,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G39,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L39,M39),1),\"\")","v":""},"",""]
[null,26,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G40,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L40,M40),1),\"\")","v":""},"",""]
[null,27,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G41,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L41,M41),1),\"\")","v":""},"",""]
[null,28,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G42,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L42,M42),1),\"\")","v":""},"",""]
[null,29,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G43,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L43,M43),1),\"\")","v":""},"",""]
[null,30,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G44,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L44,M44),1),\"\")","v":""},"",""]
[null,31,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G45,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L45,M45),1),\"\")","v":""},"",""]
[null,32,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G46,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L46,M46),1),\"\")","v":""},"",""]
[null,33,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G47,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L47,M47),1),\"\")","v":""},"",""]
[null,34,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G48,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L48,M48),1),\"\")","v":""},"",""]
[null,35,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G49,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L49,M49),1),\"\")","v":""},"",""]
[null,36,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G50,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L50,M50),1),\"\")","v":""},"",""]
[null,37,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G51,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L51,M51),1),\"\")","v":""},"",""]
[null,38,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G52,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L52,M52),1),\"\")","v":""},"",""]
[null,39,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G53,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L53,M53),1),\"\")","v":""},"",""]
[null,40,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G54,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L54,M54),1),\"\")","v":""},"",""]
[null,41,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G55,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L55,M55),1),\"\")","v":""},"",""]
[null,42,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G56,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L56,M56),1),\"\")","v":""},"",""]
[null,43,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G57,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L57,M57),1),\"\")","v":""},"",""]
[null,44,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G58,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L58,M58),1),\"\")","v":""},"",""]
[null,45,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G59,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L59,M59),1),\"\")","v":""},"",""]
[null,46,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G60,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L60,M60),1),\"\")","v":""},"",""]
[null,47,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G61,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L61,M61),1),\"\")","v":""},"",""]
[null,48,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G62,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L62,M62),1),\"\")","v":""},"",""]
[null,49,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G63,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L63,M63),1),\"\")","v":""},"",""]
[null,50,null,"",null,null,"","",{"$f":"IFERROR(VLOOKUP(G64,需要量!$A$2:$B$313,2,FALSE),\"\")","v":""},{"$f":"IFERROR(LARGE((L64,M64),1),\"\")","v":""},"",""]

{"sheet":"導管","index":25,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"INPUTDATA","index":26,"n_rows":29,"n_cols":15,"rows_kept":29,"cut":false,"hidden":false,"merged":[]}
[]
[]
[1]
[]
[2]
[]
[3]
[null,null,null,null,null,null,null,null,null,null,"表１　KG-POLE（Sheet(\"パイプデータ\"）で使用）"]
[4,null,null,null,null,null,null,null,null,"内径D(cm)（HLOOKUP関数参照数値）",0,5,8,10,15]
[null,null,null,null,null,"流量係数一覧表",null,null,null,"内径D(cm)",{"$f":"K9  & \"<D ≦\" & L9","v":"0<D ≦5"},{"$f":"L9  & \"<D ≦\" & M9","v":"5<D ≦8"},"8<D ≦10","10<D ≦15",{"$f":"O9 & \"<D \"","v":"15<D "}]
[5,null,null,null,null,"No.","圧力","名称","流量係数　K(D)","流量係数（ポールの係数）",0.70699999999999996,0.70699999999999996,0.70699999999999996,0.70699999999999996,0.70699999999999996]
[null,null,null,null,null,1,"低圧","KG-Pole","内径に応じた係数（表１参照）"]
[6,null,null,null,null,2,"低圧","Cox","0.653"]
[null,null,null,null,null,3,"低圧","Molesworth","0.523"]
[7,"一般需要量の合計(m3/D)",null,null,null,4,"低圧","Spitzglass","1/SQRT(1+9.15/D+0.012D)"]
[null,{"$f":"需要量!G4","v":13440},null,null,null,5,"低圧","Unwin","0.888/SQRT(1+4.35/D)"]
[8,"大口需要量の合計(m3/D)",null,null,null,6,"低圧","米花","0.837/SQRT(1+4.35/D)"]
[null,0,null,null,null,7,"低圧","その他","A1/SQRT(1+A2/D+A3*D)"]
[9,"大口需要ノード数（100個以内）",null,null,null,8,"低圧","その他","A1"]
[null,0,null,null,null,9,"中圧","Cox","52.31"]
[10,"ガバナ製造量の合計（m3/D)",null,null,null,10,"中圧","Pittsbugh","57.79"]
[null,{"$f":"SUM(需要量!C2:C242)","v":560},null,null,null,11,"中圧","Rix","57.96"]
[11,"流量係数 K(D) ",null,null,null,12,"中圧","Towl","60.16"]
[null,1,null,null,null,13,"中圧","Unwin","61.05/SQRT(1+4.35/D)"]
[12,"流量補正係数（K(D)にかける流量補正係数　a",null,null,null,14,"中圧","Oliphant","51.12*(1+SQRT(D)/47.81)"]
[null,"（K(D)にかける流量補正係数 a （通常 a=1 : K=K(D)×a）",null,null,null,15,"中圧","Weymouth","37.67D^(1/6)"]
[null,1,null,null,null,16,"中圧","California","33.01D^(1/6)"]
[13,"送出量（m3/h）"]
[null,{"$f":"SUM(需要量!C2:C242)","v":560}]

{"sheet":"絵 (3)","index":27,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"絵 (2)","index":28,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"絵","index":29,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"製造曲線","index":30,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"大口需要曲線","index":31,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"一般需要曲線","index":32,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"非定常解析結果","index":33,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"No.2G停止解析結果","index":34,"n_rows":33,"n_cols":40,"rows_kept":33,"cut":false,"hidden":false,"merged":[]}
["＊＊＊No.2ガバナ停止解析結果＊＊＊",null,null,null,null,null,null,null,"＊＊　全ノードデータ　　＊＊",null,null,null,null,null,null,null,null,"＊＊　大口ノードデータ　　＊＊",null,null,null,null,null,null,null,null,"＊＊　パイプデータ　　＊＊",null,null,null,null,null,null,null,null,"＊＊　口径別延長集計　　＊＊"]
["FILE NAME: "]
[" DATE: ","R4/12/12",null,null,null,null,null,null,"ノードID","標高(m)","需要量(m3/h)",null,"圧力(ｋPa)",null,null,null,null,"ノードID",null,"需要量(m3/h)",null,"圧力(ｋPa)",null,null,null,null,"ﾊﾟｲﾌﾟ","上流","下流","内径","延長","流量","ﾊﾟｲﾌﾟ幾何容積",null,null,"口径（A)",null,"本数",null,"合計延長(m)"]
[" TIME: ","16:35:34","->","16:35:34",null,null,null,null,"N001",30,30,null,2.1019999999999999,0.13694398105144501,2.2389999999999999,null,null,"合計",null,0,null,null,null,null,null,null,"ID","ﾉｰﾄﾞID","ﾉｰﾄﾞID","(mm)","(m)","(m3/h)","(m3)",null,null,"50未満",null,0,null,0]
[null,null,null,null,null,null,null,null,"N002",30,60,null,-0.27200000000000002,0.13694398105144501,-0.13500000000000001,null,null,null,null,null,null,null,null,null,null,null,"P001","N001","N002",5,50,108.7,9.8000000000000004E-2,null,null,50,null,6,null,210]
[null,null,null,null,null,null,null,null,"N003",20,210,null,-0.748,9.1295987367630005E-2,-0.65700000000000003,null,null,null,null,null,null,null,null,null,null,null,"P002","N002","N003",5,50,48.7,9.8000000000000004E-2,null,null,100,null,1,null,30]
[null,null,null,null,null,null,null,null,"N004",10,150,null,1.4330000000000001,4.5647993683815002E-2,1.4790000000000001,null,null,null,null,null,null,null,null,null,null,null,"P003","N004","N003",5,30,134.5,5.8999999999999997E-2,null,null,150,null,0,null,0]
[null,null,null,null,null,null,null,null,"N005",30,80,null,-7.0999999999999994E-2,0.13694398105144501,6.6000000000000017E-2,null,null,null,null,null,null,null,null,null,null,null,"P004","N001","N004",10,30,421.3,0.23599999999999999,null,null,200,null,2,null,100]
[null,null,null,null,null,null,null,null,"N006",20,30,null,-0.71899999999999997,9.1295987367630005E-2,-0.628,null,null,null,null,null,null,null,null,null,null,null,"P005","N004","N005",5,20,136.80000000000001,3.9E-2,null,null,250,null,0,null,0]
[null,null,null,null,null,null,null,null,"エナジー",30,0,null,2.1629999999999998,0.13694398105144501,2.2999999999999998,null,null,null,null,null,null,null,null,null,null,null,"P006","N005","N006",5,50,56.8,9.8000000000000004E-2,null,null,300,null,0,null,0]
[null,null,null,null,null,null,null,null,"ソリューション",30,0,null,-0.71899999999999997,0.13694398105144501,-0.58199999999999996,null,null,null,null,null,null,null,null,null,null,null,"P007","N006","N003",5,10,26.8,0.02,null,null,350,null,0,null,0]
[null,null,null,null,null,null,null,null,"需要量合計(m3/h)",null,560,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P101","エナジー","N001",20,50,560,1.571,null,null,400,null,0,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"P102","N006","ソリューション",20,50,0,1.571,null,null,450,null,0,null,0]
["＊＊　流量係数　K=K(D)*a ＊＊",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,340,null,3.79,null,null,500,null,0,null,0]
["1 Pole        K(D) = KG-Pole",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,550,null,0,null,0]
["流量補正係数　a= ",null,1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,600,null,0,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,650,null,0,null,0]
["許容誤差",null,1E-8,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null," 700以上",null,0,null,0]
["設定最大繰り返し計算数",null,30000]
["繰り返し計算数",null,21]
[]
["比重",null,0.64]
["総ノード数",null,8]
["一般ノード数",null,8]
["大口ノード数",null,0]
["パイプ数",null,9]
["ガバナ数",null,1]
[]
[]
["＊＊　ガバナデータ　　＊＊"]
["ガバナID","ガバナ設定圧力（ｋPa）","ガバナ標高(m)","ガバナ標高補正圧力(kPa)","ガバナ標高補正後圧力(kPa)","ガバナ送出量(m3/h)"]
["エナジー",2.1629999999999998,30,0.13700000000000001,2.2999999999999998,560]
["ガバナ送出量合計(m3/h)",null,null,null,null,560]

{"sheet":"Sheet23","index":35,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet22","index":36,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet21","index":37,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}